# SOP-114 — Pressure Relief Device Setting & Testing

Revision 6    Effective: 01-Jan-2026    Owner: Inspection Dept

# 4. Set Pressure Requirements

All safety relief valves protecting atmospheric storage tanks in CDU-II shall be set at 14.0 barg unless a documented deviation exists, approved by the Head of Inspection.

Set pressure shall be verified by bench test at intervals not exceeding 24 months. Test records shall be retained for 10 years.

# 5. Thickness Acceptance

Minimum acceptable shell thickness shall be computed per API 653 Section 4.3. Measured thickness below nominal requires engineering evaluation but does not by itself constitute a rejection.